## GXT4 500VA-3000VA
Watts |  |  |  |  | Approximate Battery Runtime
0 |  | Unit |  | % Load | INTERNAL | (1) EXTERNAL | (2) EXTERNAL | (3) EXTERNAL | (4) EXTERNAL | (5) EXTERNAL | (6) EXTERNAL
|  | GXT3-500RT120 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
|  | GXT3-700RT120 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
Desired Runtime |  | GXT3-1000RT120 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
0 |  | GXT3-1500RT120 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
| min | GXT3-2000RT120 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
|  | GXT3-3000RT120 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
|  | GXT3-3000RT208 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
|  | = UPS is Over Loaded |  |  | = UPS Supports Load But Battery Runtime Does Not Meet Expectations |  |  |  |  | = UPS Supports Load & Battery Runtime Expectations Are Met
|  | * | Battery runtimes are approximate and load is rounded up to the nearest 10%
Battery Quantity | Percent Load | 120VAC RT Models | [5 empty] | 208VAC RT Model
|  | 500VA | 700VA | 1000VA | 1500VA | 2000VA | 3000VA | 3000VA
Internal Battery | 10% | 128 | 105 | 90 | 123 | 92 | 82 | 92
| 20% | 82 | 61 | 37 | 52 | 38 | 38 | 39
| 30% | 41 | 37 | 30 | 34 | 23 | 23 | 23
| 40% | 38 | 32 | 23 | 23 | 16 | 16 | 16
| 50% | 34 | 27 | 17 | 18 | 12 | 12 | 11
| 60% | 31 | 22 | 14 | 14 | 9 | 9 | 9
| 70% | 27 | 18 | 11 | 11 | 7 | 7 | 7
| 80% | 23 | 15 | 9 | 9 | 5 | 5 | 5
| 90% | 20 | 13 | 8 | 7 | 4 | 4 | 4
| 100% | 17 | 11 | 7 | 6 | 3 | 3 | 3
Internal Battery + 1 External Battery Cabinet | 10% | 448 | 426 | 332 | 335 | 303 | 224 | 303
| 20% | 329 | 302 | 165 | 162 | 140 | 137 | 139
| 30% | 223 | 163 | 137 | 129 | 96 | 95 | 95
| 40% | 166 | 144 | 108 | 96 | 66 | 66 | 65
| 50% | 153 | 125 | 92 | 72 | 49 | 49 | 48
| 60% | 139 | 106 | 74 | 54 | 38 | 41 | 41
| 70% | 125 | 94 | 61 | 46 | 33 | 34 | 34
| 80% | 108 | 78 | 49 | 38 | 28 | 27 | 27
| 90% | 100 | 69 | 40 | 34 | 23 | 23 | 25
| 100% | 92 | 60 | 38 | 31 | 20 | 21 | 21
Internal Battery + 2 External Battery Cabinet | 10% | 480 | 480 | 456 | 451 | 431 | 427 | 431
| 20% | 454 | 433 | 331 | 318 | 207 | 202 | 205
| 30% | 429 | 327 | 222 | 187 | 150 | 149 | 149
| 40% | 333 | 265 | 166 | 151 | 124 | 124 | 123
| 50% | 309 | 201 | 152 | 131 | 97 | 98 | 97
| 60% | 225 | 164 | 137 | 107 | 75 | 76 | 75
| 70% | 201 | 153 | 122 | 91 | 61 | 62 | 62
| 80% | 166 | 142 | 105 | 74 | 50 | 50 | 50
| 90% | 159 | 131 | 95 | 64 | 41 | 45 | 46
| 100% | 151 | 120 | 79 | 53 | 38 | 41 | 41
Internal Battery + 3 External Battery Cabinet | 10% | 480 | 480 | 480 | 480 | 455 | 452 | 455
| 20% | 480 | 461 | 441 | 426 | 326 | 323 | 325
| 30% | 458 | 438 | 336 | 312 | 197 | 196 | 195
| 40% | 442 | 344 | 305 | 198 | 155 | 155 | 154
| 50% | 426 | 322 | 209 | 160 | 136 | 136 | 135
| 60% | 338 | 300 | 167 | 145 | 111 | 112 | 112
| 70% | 322 | 213 | 157 | 130 | 96 | 98 | 98
| 80% | 305 | 189 | 146 | 111 | 78 | 79 | 79
| 90% | 225 | 163 | 135 | 99 | 68 | 70 | 70
| 100% | 209 | 155 | 124 | 83 | 56 | 60 | 60
Internal Battery + 4 External Battery Cabinet | 10% | 480 | 480 | 480 | 480 | 480 | 466 | 480
| 20% | 480 | 480 | 459 | 446 | 424 | 421 | 423
| 30% | 480 | 457 | 435 | 341 | 308 | 307 | 307
| 40% | 460 | 441 | 339 | 309 | 192 | 192 | 191
| 50% | 448 | 424 | 316 | 204 | 157 | 158 | 157
| 60% | 436 | 336 | 221 | 164 | 142 | 143 | 142
| 70% | 424 | 318 | 199 | 153 | 126 | 128 | 128
| 80% | 340 | 301 | 166 | 141 | 107 | 109 | 109
| 90% | 327 | 213 | 158 | 130 | 95 | 97 | 98
| 100% | 315 | 197 | 149 | 112 | 79 | 81 | 81
Internal Battery + 5 External Battery Cabinet | 10% | 480 | 480 | 480 | 480 | 480 | 480 | 480
| 20% | 480 | 480 | 466 | 458 | 441 | 439 | 440
| 30% | 480 | 464 | 446 | 432 | 333 | 332 | 331
| 40% | 467 | 451 | 427 | 333 | 225 | 225 | 224
| 50% | 457 | 438 | 341 | 306 | 188 | 190 | 188
| 60% | 447 | 424 | 322 | 207 | 158 | 159 | 159
| 70% | 438 | 343 | 303 | 167 | 145 | 147 | 147
| 80% | 428 | 329 | 212 | 158 | 133 | 135 | 135
| 90% | 390 | 315 | 193 | 148 | 120 | 122 | 122
| 100% | 341 | 300 | 166 | 139 | 104 | 107 | 106
Internal Battery + 6 External Battery Cabinet | 10% | 480 | 480 | 480 | 480 | 480 | 480 | 480
| 20% | 480 | 480 | 480 | 467 | 452 | 450 | 451
| 30% | 480 | 480 | 458 | 445 | 422 | 421 | 421
| 40% | 480 | 462 | 442 | 422 | 319 | 319 | 318
| 50% | 467 | 451 | 426 | 327 | 216 | 218 | 216
| 60% | 459 | 440 | 342 | 304 | 185 | 188 | 186
| 70% | 451 | 428 | 326 | 208 | 159 | 160 | 160
| 80% | 442 | 370 | 309 | 184 | 148 | 149 | 150
| 90% | 434 | 336 | 221 | 161 | 137 | 139 | 139
| 100% | 426 | 324 | 204 | 153 | 126 | 129 | 129

## GXT4 5kVA-10kVA
Watts |  |  |  |  | Approximate Battery Runtime
0 |  | Unit |  | % Load | INTERNAL | (1) EXTERNAL | (2) EXTERNAL | (3) EXTERNAL | (4) EXTERNAL | (5) EXTERNAL | (6) EXTERNAL
|  | GXT4-5000RT208 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
|  | GXT4-6000RT208 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
Desired Runtime |  | GXT4-8000RT208 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
0 |  | GXT4-10000RT208 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
| min | GXT4-6000RTL630 |  | 0% | No Load | No Load | No Load | No Load | No Load | No Load | No Load
|  | = UPS is Over Loaded |  |  | = UPS Supports Load But Battery Runtime Does Not Meet Expectations |  |  |  |  | = UPS Supports Load & Battery Runtime Expectations Are Met
|  | * | Battery runtimes are approximate and load is rounded up to the nearest 10%
Battery Quantity | Percent Load | 208/120VAC RT Models |  |  |  | 208VAC RT Model
|  | 5kVA | 6kVA | 8kVA | 10kVA | 6kVA (L630)
Internal Battery | 10% | 129 | 106 | 144 | 112 | 100
| 20% | 52 | 46 | 69 | 48 | 50
| 30% | 36 | 27 | 43 | 30 | 38
| 40% | 25 | 19 | 28 | 21 | 26
| 50% | 18 | 14 | 22 | 16 | 19
| 60% | 14 | 11 | 18 | 12 | 15
| 70% | 11 | 9 | 14 | 10 | 12
| 80% | 9 | 7 | 11 | 8 | 10
| 90% | 8 | 5 | 10 | 6 | 9
| 100% | 6 | 5 | 8 | 5 | 8
Internal Battery + 1 External Battery Cabinet | 10% | 217 | 188 | 312 | 201 | 200
| 20% | 131 | 108 | 145 | 120 | 132
| 30% | 82 | 67 | 102 | 73 | 98
| 40% | 53 | 46 | 71 | 49 | 73
| 50% | 45 | 37 | 50 | 40 | 52
| 60% | 37 | 28 | 43 | 31 | 46
| 70% | 28 | 23 | 36 | 26 | 40
| 80% | 25 | 19 | 28 | 21 | 34
| 90% | 21 | 16 | 26 | 18 | 28
| 100% | 18 | 14 | 22 | 16 | 25
Internal Battery + 2 External Battery Cabinet | 10% | 341 | 321 | 428 | 330 | 345
| 20% | 165 | 152 | 199 | 157 | 205
| 30% | 133 | 109 | 146 | 121 | 150
| 40% | 100 | 77 | 113 | 82 | 124
| 50% | 74 | 53 | 92 | 64 | 101
| 60% | 53 | 47 | 71 | 49 | 80
| 70% | 48 | 40 | 53 | 43 | 68
| 80% | 42 | 33 | 48 | 37 | 52
| 90% | 37 | 27 | 43 | 31 | 49
| 100% | 31 | 25 | 38 | 27 | 46
Internal Battery + 3 External Battery Cabinet | 10% | 438 | 424 | 450 | 430 | 433
| 20% | 221 | 192 | 314 | 204 | 316
| 30% | 158 | 143 | 180 | 149 | 196
| 40% | 134 | 109 | 147 | 122 | 157
| 50% | 106 | 82 | 126 | 95 | 138
| 60% | 83 | 68 | 103 | 73 | 113
| 70% | 70 | 51 | 82 | 60 | 101
| 80% | 53 | 46 | 71 | 49 | 83
| 90% | 49 | 41 | 60 | 44 | 75
| 100% | 45 | 36 | 50 | 40 | 67
Internal Battery + 4 External Battery Cabinet | 10% | 454 | 442 | 463 | 447 | 456
| 20% | 323 | 300 | 340 | 310 | 420
| 30% | 194 | 161 | 218 | 165 | 304
| 40% | 153 | 138 | 164 | 144 | 200
| 50% | 134 | 110 | 147 | 122 | 160
| 60% | 110 | 92 | 130 | 99 | 145
| 70% | 95 | 74 | 109 | 79 | 130
| 80% | 77 | 62 | 96 | 68 | 111
| 90% | 67 | 50 | 79 | 53 | 102
| 100% | 53 | 46 | 71 | 49 | 93
Internal Battery + 5 External Battery Cabinet | 10% | 464 | 454 | 480 | 459 | 466
| 20% | 343 | 324 | 429 | 332 | 430
| 30% | 224 | 194 | 316 | 206 | 332
| 40% | 166 | 153 | 203 | 158 | 225
| 50% | 150 | 134 | 161 | 140 | 195
| 60% | 134 | 110 | 147 | 122 | 161
| 70% | 112 | 95 | 133 | 102 | 149
| 80% | 100 | 77 | 113 | 82 | 137
| 90% | 82 | 67 | 102 | 73 | 126
| 100% | 74 | 53 | 91 | 64 | 110
Internal Battery + 6 External Battery Cabinet | 10% | 480 | 463 | 480 | 467 | 480
| 20% | 430 | 341 | 442 | 420 | 452
| 30% | 317 | 219 | 334 | 301 | 423
| 40% | 204 | 164 | 227 | 183 | 321
| 50% | 162 | 148 | 191 | 153 | 227
| 60% | 148 | 131 | 159 | 138 | 195
| 70% | 134 | 110 | 147 | 122 | 162
| 80% | 120 | 97 | 135 | 104 | 152
| 90% | 103 | 80 | 122 | 92 | 142
| 100% | 92 | 71 | 107 | 77 | 133